## Sheet1
Client PO Number | Client PO Date | Party Name | Region | Tax Rate | Project Closure Date | Mode Of Payment | Jurisdiction | Freight | Delivery | Warranty | Other T&C
UCPL/BNG/ICMR/WO/030 | 2025-01-20 | UDRA CONSTRUCTION PRIVATE LIMITED | Bangalore | 18 |  | Immediate | Bangalore | Included | Immediate | 12 months from the date of delivery
Sl No | Description |  |  |  | Model No. | HSN | SAC | Qty | Unit | Supply Price | Service Price
A | FIRE ALARM PANEL & ACTIVE REPEATER PANEL: | [6 empty] | 0 | Heading | 0 | 0
1 | Fire ALARM PANEL | [6 empty] | 0 | Heading | 0 | 0
| Supplying, installing, testing and commissioning approved make Microprocessor based 8 loop, Networkable Addressable Fire Alarm Control Panel with minimum 600 characters LCD display or 10 inch colourful touchscreen display, 3000 trouble events including 1000 alarm log history events, Self Programmable alphanumeric keypad for programming. The panel shall be expandable upto 10 Loops. Each loop shall have a capacity of minimum 120 detectors & 120 other devices exculding 20% spare. The panel shall work in fail safe mode and shall perform detection and annunciation in case of CPU failure, Products not having this feature may offer Redundant CPU. Four access levels, flash EPROM, 240 volts AC power supply, automatic battery charger, 24 volts sealed lead acid batteries sufficient for 48 hours normal working and 30 mins in alarm condition with the charging capacity of 200AH. The panel shall be capable of self programing without any dependancy on dongle or programming software. Quoted rate shall include supply of necessary software & hardware for progamming the panel with all necessary licence, if required. Panel shall have Modbus over IP protocol for future integration with BMS. However, for present arrangement FA system will be standalone with 24x7 monitoring. The panel shall have provision for remote accessibility in order to perform the operations (monitoring & Control function) through mobile app on a cloud platform/solution. Panel shall be listed under UL guideline to standard of UL864-10th Edition & FM Approved. | [6 empty] | 1 | Nos | 583852 | 70000
2 | NETWORK REPEATER PANEL | [6 empty] | 0 | Heading | 0 | 0
| Supplying, installing, testing and commissioning approved make Programmable Network Repeater Panel with Programming Keypad, mapping minimum 2,00,000 points on network. The NRP shall act as an independent node communicating on the network and shall not be dependant on the Fire Panel CPU for operation. Failure of Fire Panel CPU shall not result in failure of NRP operation. The Panel shall be UL & FM Listed. | [6 empty] | 1 | Nos | 92110 | 10000
B | Software & Gateways | [6 empty] | 0 | Heading | 0 | 0
1 | Supply, Installation, testing and commsissioning of Graphics User Interface for Monitoring & Control of complete Fire, Voice Evacuation & Telephone Talkback System. The GUI based main network software shall network with other panels on True Peer-to-Peer network. It shall be capable of graphically representing each facility being monitored with floor plans and icons depicting the actual locations of the various systems, and / or sensors’ locations. It shall have the facility to change the sensitivity of any detector. The software shall be capable of monitoring 200 Nodes with 100 Mbps Transmission rate on Fibre Optics Network and 12 Mbps Transmission on cable and 2,50,000 network points. The software shall be capable to Monitor & Control all the Digital Voice Evactuation as well as 2 way communication from main control room using voice signals over Fire Network along with the Fire detection signal. The Graphic workstation shall act as an independent node communicating on the peer to peer network and shall not be dependant on the Fire Panel CPU for operation. Failure of Fire Panel CPU shall not result in failure of GUI. UL & FM APPROVED | [6 empty] | 1 | Nos | 336660 | 25000
2 | Supplying, installing ,testing and commissioning of branded Fire Alarm Graphic Workstation for the Above mention GUI software. Intel i7 + Processor or Latest Technology with min 8GB (4 x 2GB) 1600MHz DDR3 Non-ECC,high speed 7.5K rpm 2 TB SATA hard disk, Enhanced 2 GB Integrated Intel Graphics Media Accelerator ,Integrated 10/100/1000 Ethernet NIC(Dual Giga Bite Ethernet Ports),Cordless 104 keys window 98 keyboard & Mouse, DVD Combo Drive etc. Cost should be With Life time licenses for Windows 8 License or any latest version compatible with BMS software , Anti virus & All other related software along with High resolution 24" LED HD Flat Screen with HDMI, PC inputs, complete wall mounted / table mounted Brackets as per Specification. | [6 empty] | 1 | Nos | 152630 | 10000
C | Detectors | [6 empty] | 0 | Heading | 0 | 0
2 | Supply, installation, testing and commissioning addressable multi-criteria photo-thermal detector with sensitivity range of 0.5 to 4.0% obs/ft. Intelligent multi criteria detection device shall include the ability to combine signal of the thermal sensor with photoelectric signal in an effort to react hastily in the event of a fire situation. Detector shall be able to distinguish between a fire and a false alarm condition. Detector which have addressing in base shall be include dust boot of same make.The detector shall have twin bi-color LED for 360 deg viewing. UL268, 7th Edition listed & FM approved- for detector & base along with the end termination of cable to junction boxes using single compression brass type cable glands & pin type tinned copper lugs etc (Above False Ceiling) Designed to meet UL268, 7th Edition (ABOVE FALSE CEILING)UL & FM APPROVED | [6 empty] | 175 | Nos | 2920 | 400
3 | Supply, installation, testing and commissioning addressable multi-criteria photo-thermal detector with sensitivity range of 0.5 to 4.0% obs/ft. Intelligent multi criteria detection device shall include the ability to combine signal of the thermal sensor with photoelectric signal in an effort to react hastily in the event of a fire situation. Detector shall be able to distinguish between a fire and a false alarm condition. Detector which have addressing in base shall be include dust boot of same make.The detector shall have twin bi-color LED for 360 deg viewing. UL268, 7th Edition listed & FM approved- for detector & base along with the end termination of cable to junction boxes using single compression brass type cable glands & pin type tinned copper lugs etc (Above False Ceiling Designed to meet UL268, 7th Edition (BELOW FALSE CEILING)UL & FM APPROVED | [6 empty] | 175 | Nos | 2760 | 400
4 | Supply, Installation, testing and commsissioning of Addressable Rate of Rise Heat Detector rated at 8.3 deg C/min. The detector shall have twin bi-colour LED for 360 deg viewing Detector which have addressing in base shall be include dust boot of same make.Addressing shall be with user friendly rotary decimal switches. (ABOVE FALSE CEILING)UL & FM APPROVED | [6 empty] | 4 | Nos | 2610 | 400
5 | Addressable Duct Smoke Detector. The duct detector shall have an air velocity rating from 100 to 4000 ft/min. The detector shall have twin bi-colour LED for 360 deg viewing. Addressing shall be with user friendly rotary decimal switches.UL & FM APPROVED | [6 empty] | 3 | Nos | 12600 | 500
6 | Multi-criteria photo-thermal detector (ABOVE FALSE CEILING)DETECTORS INSTALLED IN BSL-3 AEREAS ARE IP 65 RATED | [6 empty] | 52 | Nos | 2920 | 400
7 | Multi-criteria photo-thermal detector (BELOW FALSE CEILING)DETECTORS INSTALLED IN BSL-3 AEREAS ARE IP 65 RATED | [6 empty] | 52 | Nos | 2760 | 400
D | Modules | [6 empty] | 0 | Heading | 0 | 0
6 | Supply, Installation, testing and commsissioning of Addressable Manual Call Point (Pull down Type/ Break Glass Type ). The device shall have an LED which shall blink in normal state & get steady on activation to monitor the heath status of the device. .The quoted rate shall include metal boxes to fix the MCP. UL & FM APPROVED | [6 empty] | 15 | Nos | 3120 | 400
7 | Supply, Installation, testing and commsissioning of Addressable Control Module for Sounders / Strobes / Sounder cum Strobes. The control module shall provide supervised NAC output rated at 24v DC, 2A. The device shall have an LED which shall blink in normal state & get steady on activation to monitor the heath status of the device. Addressing shall be with user friendly rotary decimal switches. Module shall be supplied with mounting plate from OEM for ease of installation & maintenance. UL & FM APPROVED | [6 empty] | 12 | Nos | 3710 | 400
8 | Supply, Installation, testing and commsissioning of Addressable Relay Module for AHU, Access Control, Lifts, Staircase Pressurization, Fire Suppression & other Third Party Outputs. The relay module shall provide contact rated at 24v DC, 2A. The device shall have an LED which shall blink in normal state & get steady on activation to monitor the heath status of the device. Addressing shall be with user friendly rotary decimal switches. Module shall be supplied with mounting plate from OEM for ease of installation & maintenance.UL & FM APPROVED | [6 empty] | 7 | Nos | 3710 | 400
9 | Addressable Monitor Module for Sprinklers, Panic Bars & other Third Party Inputs. The monitor module shall monitor potential free contacts. The device shall have an LED which shall blink in normal state & get steady on activation to monitor the heath status of the device. Addressing shall be with user friendly rotary decimal switches. Module shall be supplied with mounting plate from OEM for ease of installation & maintenance.UL & FM APPROVED | [6 empty] | 8 | Nos | 3180 | 400
10 | Supply, Installation, testing and commsissioning of Isolator Module for Isolating short / dewired / loose circuits with automatic resetting arrangement. Isolator Base can also be proposed, however in that case needs to be considered with each detector & module. The device shall have an LED which shall blink in normal state & get steady on activation to monitor the heath status of the device. Module shall be supplied with mounting plate from OEM for ease of installation & maintenance.UL & FM APPROVED | [6 empty] | 30 | Nos | 3000 | 400
| Notification Devices | [6 empty] | 0 | Heading | 0 | 0
16 | Supply, Installation, testing and commsissioning of Sounder cum Strobe rated at 80 dBA @ 3m for Audible annunciation and 115cd flashintg at 1 Hz for visual indication. The quoted rate shall include metal back boxes to fix the Strobe/Horn.UL Listed | [6 empty] | 12 | Nos | 4840 | 400
17 | Supply, Installation, testing and commsissioning of Sounder cum Strobe rated IP 65 | [6 empty] | 1 | Nos | 15500 | 800
18 | Supply, Installation, testing and commsissioning of Power Supply Unit: 24V DC for Notification Appliances. | [6 empty] | 2 | Nos | 6970 | 2500
19 | Supplying, installing, testing and commissioning of Response Indicator complete with all accessories etc., for above false ceiling and of monitored type. The response indicator shall be as per technical specification. | [6 empty] | 227 | Nos | 87 | 50
| Supply, Installation, Testing & Commssioning of EN54-16 compliant IP Based Digital Public Address & Voice Alarm system. The selected system devices like controllers and Paging Microphones, should use the TCP/IP technologies and build on the standard network platform to ensure expandability. | [6 empty] | 0 | Heading | 0 | 0
| Contoller: | [6 empty] | 0 | Heading | 0 | 0
1 | Supply, Installation, Testing & Commssioning of of 8 Channel & 8 Zones IP based digital Voice Alarm controller capable of handling 4000 Watts. The voice alarm controller should be able to connect directly over Ethernet. It should have functions like the audio playing, zone control, fault monitoring, log recording, volume control and amplifier switchover. The System shall be expandable type upto 2000 Zones. Individual Voice alarm controller should also have the following functions: . 255 Priorities . Time schedule broadcasts . 2 additional Channels for back up Amplifiers. . 8 trigger inputs/outputs . 8 AVC dgital input. . 5 Addressable Noise detectors per speaker zone. (Note: master slave/Master router controller concept not accepted to avoid single point failure). No of controller to be quoted as per BOQ. | [6 empty] | 1 | Nos | 329000 | 40000
| Paging Console & Music Player | [6 empty] | 0 | Heading | 0 | 0
3 | Supply, Installation, Testing & Commssioning of IP based Networkable 7 " capacitive touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Built-in monitoring loudspeaker . Detachable goose-neck microphone . LCD touchscreen display . Audio input . Power Supply - 24VDC or POE . Provision for temporary recording function . Shortcut functions - one key broadcast, volume control etc . Shall be capable of monitoring & controlling multiple zones. | [6 empty] | 1 | Nos | 218120 | 35000
4 | Supply, Installation, Testing & Commssioning of DVD Music Player with necessary accessories. | [6 empty] | 1 | Nos | 16450 | 1000
| Digital Amplifiers | [6 empty] | 0 | Heading | 0 | 0
5 | Supply, Installation, Testing & Commssioning of 1X500W Class-D Amplifier, which can provide automatic re-settable overcurrent, overload, overheating, overvoltage, under-voltage and DC protection and High Efficiency Class D Power Amplifier, 500W, 100V/70 Output, with 100 - 240 VAC input. Complaint to IEC/EN 60065:2001 (7th E) + A1:2005 = A2:2010, IEC/EN/UL 62368-1: 2014 (2nd E), EN 60065.2002 + A12006 + A11: 2008 + A2:2010 + A12:2011, EN 62368:2014, CSA C22.2 NO.62368-1-14:2014, UL 62368:2014, EN 55032:2012 with EN 55032:2012 AC 2013, EN 61000-3-2:2014, EN 61000-3-3:2013, EN 55103-2:2009, FCC part 15 subpart B | [6 empty] | 2 | Nos | 51040 | 10000
| Speakers | [6 empty] | 0 | Heading | 0 | 0
6 | Supply, Installation, Testing & Commssioning of 6W Ceiling Speaker with max SPL1M/1W 95dB . Frequency response of 125Hz-16KHz with a dispersion angle of 160 deg. The speaker should have tappings at 6W/3W/1.5W. | [6 empty] | 67 | Nos | 1170 | 400
| CCTV | [6 empty] | 0 | Heading | 0 | 0
1 | Supply, installation, testing and commissioning of CCTV WDR 2 MP IR MFZ Bullet, 2.7-13.5mm, IR: Upto 50M, IP67, IK10, POE | [6 empty] | 10 | Nos | 17500 | 400
2 | Supply, installation, testing and commissioning of CCTV WDR 2 MP IR MFZ Dome, 2.7-13.5mm, IR: Upto 50M, IP67, IK10, POE | [6 empty] | 122 | Nos | 17500 | 400
3 | Supply, installation, testing and commissioning of CCTV WDR 2MP IR Speed Dome, 30X zoom, IR: Upto 150M, IP67, IK10, POE+ | [6 empty] | 1 | Nos | 118750 | 5000
4 | Supply, installation, testing and commissioning of 32Chs NVR 4K (8 MP) Support, H.265/H.264, Stream Encryption, 8 SATA, 0 TB, NON POE, RAID | [6 empty] | 5 | Nos | 356250 | 12000
5 | Supply, installation, testing and commissioning of Video management software | [6 empty] | 1 | Nos | 58820 | 5000
6 | Video Workstation for CCTV monitoring & control with i7 processor, 16GB RAM, 1TB HDD, 2Gb Graphic card,keyboard, mouse | [6 empty] | 1 | Nos | 116470 | 5000
7 | Supply, installation, testing and commissioning of Hards disk for 30 days recording | [6 empty] | 1 | Lot | 120590 | 1250
8 | Supply, installation, testing and commissioning of 55 Inch Display | [6 empty] | 1 | Nos | 57060 | 1000
| Server Worskstation | [6 empty] | 0 | Heading | 0 | 0
1 | Client Station: i7 processor with 16 GB DDR RAM , minimum 1 TB SATA Hard Disk, 4Gb Graphics cards, Lan Card 10/100/1000 base-T, Optical Mouse, 104 Keys Keyboard, latest windows OS compatible. | [6 empty] | 2 | Nos | 117700 | 5000
2 | 32 Inch display monitor | [6 empty] | 2 | Nos | 30600 | 1000
3 | A4 Laserjet printer B/W | [6 empty] | 1 | Nos | 17700 | 1000
4.a | Web Based BMS Software meeting the requirements in the Given I/O Summary and technical specifications including configuration and facility to create / provide the graphic mapping for all I/O Summary points, Graphics, Navigation between pages, display of logs, smart alarm management and Web scheduling. The software shall be a graphically programming tool. Software shall be able to communicate with Lon works, Bacnet, Modbus devices simultaneously, with unlimited user license capacity. | [6 empty] | 1 | Nos | 282200 | 75000
4.b | SMS alert module | [6 empty] | 1 | Nos | 93400 | 15000
5 | System Integration Units of specified Make, for 3rd party integration purpose only, as required to suit the system design derived by the contractors. These units must be capable of supporting & handling multiple protocol,BACNet , MODBUS, M-Bus, LON, simultaneously. The unit must handle atleast 150 slave devices.The units shall be housed in a vandal proof, lockable & secure wall mounted MS Cabinets to be supplied along with the Controllers. The contractor shall estimate the required quantity of controllers according to their system and the quantity shall be mentioned in their offer. Cook Tanks, Chiller, Chiller Pump PLC, Steam Generations/Boiler, STP equipment, ETP equipment, HT/LT panel Breakers, PLC, Energy Meter, AHU VFD, VRV/VRF system, Lifts, Transformers, UPS, DG set, Hot water system | [6 empty] | 1 | Nos | 515000 | 75000
6 | DDC Controller with I/O module, expandable to meet the IO summary listed, The controllers shall be minimum 32 bit Double microprocessor based standalone working on TCP/IP on Bacnet IP with integral web browser, calender fundtion complete with day, month, week, year etc, real time clock & 1 second scan time. DDC working on 230V AC are preferred. The DDC's shall be capable of peer to peer communication without help of communication controller / router / system interface controller / PC and shall communicate with the building LAN directly. These shall come with lockable mounting cabinets duly powder coated connector strip, internal wiring and space to house controller & relays, connector strip step down transformer, MCB, internal wiring. (Contractor shall confirm his I/O provision w.r.t requirement on basis of data point) on AHRAE approved Bacnet protocol only. DDCs shall work on either 230V power supply or shall contain UL listed SMPS in the panel. The controllers shall have automatic IP addressing as a default setting, on power up the controller will attempt to contact a network Dynamic Host Configuration Protocol Server (DHCP server). If found the DCHP Server will allocate the IP Settings. If no DHCP server is available or one is not connected to the network, then the Controller will adopt an internal network privately negotiated addressing scheme (sometimes referred to as LINK-LOCAL addressing). DDC for chiller plant, primary pumps, secondary pumps, condenser pumps as per IO summary with 10% spare | [6 empty] | 0 | Heading | 0 | 0
6.1 | DDC Panel for Pressurization system | [6 empty] | 1 | Nos | 78200 | 7000
6.2 | DDC Panel for Fire Fighting System, UG Sumps | [6 empty] | 1 | Nos | 101200 | 9000
6.3 | DDC Panel for AHU(2 Ahus per DDC), OH Tanks | [6 empty] | 1 | Nos | 141900 | 11000
6.3 | DDC Panel for AHU(1 Ahus per DDC) | [6 empty] | 1 | Nos | 100700 | 9000
6.4 | DDC Panel for ACS Doors | [6 empty] | 1 | Nos | 105900 | 9000
7 | Supply, installation, testing, commissioning of necessary Input sensor transmitters/transducers comprising the following: | [6 empty] | 0 | Heading | 0 | 0
7.1 | Supply, Installation, Testing, Commissioning of Differential Pressure Switch with all mounting accessories | [6 empty] | 15 | Nos | 2200 | 750
7.2 | Supply, Installation, Testing, Commissioning of Duct Type Temperature & Rh combo Transmitter with all duct mounting accessories. | [6 empty] | 3 | Nos | 9900 | 750
7.3 | Supply, Installation, Testing, Commissioning of Air velocity sensor | [6 empty] | 3 | Nos | 26100 | 750
7.4 | Supply, Installation, Testing, Commissioning of Water level switch | [6 empty] | 7 | Nos | 7300 | 1250
7.5 | Supply, Installation, Testing, Commissioning of Outdoor T&RH Sensor | [6 empty] | 1 | Nos | 7700 | 1750
1 | Supply, Installation, Testing and Commssioining of Client station for ACS monitoring i7, 16GB RAM, 1TB HDD with keyboard and mouse | [6 empty] | 1 | Nos | 105890 | 5000
2 | Supply, Installation, Testing and Commssioining of 32 inch 24/7 Monitor | [6 empty] | 1 | Nos | 37650 | 1000
3 | Supplying, Installation, Testing & Commissioning of the Access control and basic Attendnace Software[First IN & Last Out],ntuitive web interface for access management, with embedded Help tool ,Unrestricted number of cardholders and system users ,Unrestricted number of sites and access points ,NOTIFICATIONS AND REPORTING Email, SMS ,INTERACTIVE FLOOR PLANS ,ELEVATOR CONTROL ,PHOTO ID PRODUCTION , LOCKDOWN , Two Card rule,CUSTOM CARDHOLDER FIELD TEMPLATES , TRACKING AND MUSTER REPORTS,GUARD TOUR REPORTS and should support Fire intergartion ,Supports VMWare 6.5 to help leverage existing IT infrastructure and server assets and intergrated visitor management system | [6 empty] | 1 | Nos | 400000 | 50000
4 | Supply , Installation , Testing and commissioning of 2 reader controller panel with power supply unit and enclouser, Processor ARM9, 600MHz with 6 Supervised inputs, 4 Relay outputs ,card format 8, Time Zones 127,access level 128,holiday 255, Antipassback Hard/Soft,Cardholder capacity: 100,000,Transaction storage: 100,000 with built in TCP/IP ,certification CE, UAE RoHS | [6 empty] | 15 | Nos | 32500 | 2500
5 | Supply, Installation, Testing and Commssioining of Muliticlass card reader which can support Seos, iCLASS SE®, iCLASS SR®, iCLASS®, MIFARE Classic, MIFARE DESFire EV1/EV2, FeliCa™ & Contactless e-Purse Application Specification (CEPAS), Mobile Credentials powered by Seos (HID Mobile Access),HID Proximity®, Indala® Proximity, AWID Proximity, and EM Proximity,Mobile Credentials powered by Seos® (HID Mobile Access) | [6 empty] | 15 | Nos | 20000 | 1250
6 | Supply, Installation, Testing and Commssioining iclass Smart Card Contactless complete as per specification | [6 empty] | 100 | Nos | 200 | 50
7 | Supply, Installation, Testing and Commssioining Electromagnetic lock | [6 empty] | 0 | Heading | 0 | 0
a | Double Leaf Door - 1200lbs | [6 empty] | 6 | Nos | 15410 | 2000
b | Single Door Leaf - 600lbs | [6 empty] | 9 | Nos | 3850 | 1250
8 | Supply, Installation, Testing and Commssioining no touch exit switch | [6 empty] | 15 | Nos | 1150 | 500
9 | Supply, Installation, Testing and Commssioining Emergency door release switch | [6 empty] | 15 | Nos | 670 | 250
10 | Supply, Installation, Testing and Commssioining Magnetic contact | [6 empty] | 21 | Nos | 329 | 150
| Door interlocking system with ACS for shower and change room | [6 empty] | 0 | Heading | 0 | 0
7 | 4 Door interlock controller | [6 empty] | 4 | Nos | 17640 | 3000
8 | Supply, Installation, Testing and Commssioining Electromagnetic lock Single Door Leaf - 600lbs | [6 empty] | 12 | Nos | 3850 | 1250
9 | Door Contact Sensor | [6 empty] | 12 | Nos | 180 | 100
10 | Supply, Installation, Testing and Commssioining Emergency door release switch | [6 empty] | 12 | Nos | 670 | 250
11 | Supply, Installation, Testing and Commssioining no touch exit switch | [6 empty] | 24 | Nos | 1150 | 500
1 | Supplying, installing, testing and commissioning approved make BACNET Gateway for communication with BMS / Other Utilities. Single BACNET shall support minimum 14 fully loaded FACP/400000 objects. BACNET Gateway shall act as an independent node communicating on the peer to peer network and shall not be dependant on the Fire Panel CPU for operation. Failure of Fire Panel CPU shall not result in failure of BACNET Gateway. UL 864 10th edition | [6 empty] | 1 | Nos | 228680 | 50000
2 | Additional costing for Talk back addition to the Fire Alarm Panel | [6 empty] | 1 | Nos | 350000 | 50000
3 | Supplying, installing, testing and commissioning Fire Fighting Jack with telephone module | [6 empty] | 10 | Nos | 7480 | 1250
4 | Supplying, installing, testing and commissioning Fire fighter telphone | [6 empty] | 10 | Nos | 16916 | 1250
5 | Addressable Duct Smoke Detector. The duct detector shall have an air velocity rating from 100 to 4000 ft/min. The detector shall have twin bi-colour LED for 360 deg viewing. Addressing shall be with user friendly rotary decimal switches.UL & FM APPROVED | [6 empty] | 3 | Nos | 12600 | 500
D | CABLES & CONDUITS: | [6 empty] | 0 | Heading | 0 | 0
1 | Supply, Installation, testing and commsissioning of Public address system software wth BMS integration provision. This should include server and client licence. | [6 empty] | 1 | Mtrs | 674667 | 75000
2 | Supply, Installation, testing and commsissioning of Server for the above software | [6 empty] | 1 | Mtrs | 533334 | 25000
3 | Supply, Installation, testing and commsissioning of work station for the above software | [6 empty] | 1 | Mtrs | 154667 | 10000
| Supply, Installation, Testing & Commssioning of EN54-16 compliant IP Based Digital Public Address & Voice Alarm system. The selected system devices like controllers and Paging Microphones, should use the TCP/IP technologies and build on the standard network platform to ensure expandability. | [6 empty] | 0 | Heading | 0 | 0
| Contoller: | [6 empty] | 0 | Heading | 0 | 0
1 | Supply, Installation, Testing & Commssioning of of 8 Channel & 8 Zones IP based digital Voice Alarm controller capable of handling 4000 Watts. The voice alarm controller should be able to connect directly over Ethernet. It should have functions like the audio playing, zone control, fault monitoring, log recording, volume control and amplifier switchover. The System shall be expandable type upto 2000 Zones. Individual Voice alarm controller should also have the following functions: . 255 Priorities . Time schedule broadcasts . 2 additional Channels for back up Amplifiers. . 8 trigger inputs/outputs . 8 AVC dgital input. . 5 Addressable Noise detectors per speaker zone. (Note: master slave/Master router controller concept not accepted to avoid single point failure). No of controller to be quoted as per BOQ. | [6 empty] | 1 | Nos | 329000 | 40000
| Paging Console & Music Player | [6 empty] | 0 | Heading | 0 | 0
3 | Supply, Installation, Testing & Commssioning of IP based Networkable 7 " capacitive touch screen paging station for selection of zones, supervision of system status, setting of scheduled broadcasts with the following functions: . Built-in monitoring loudspeaker . Detachable goose-neck microphone . LCD touchscreen display . Audio input . Power Supply - 24VDC or POE . Provision for temporary recording function . Shortcut functions - one key broadcast, volume control etc . Shall be capable of monitoring & controlling multiple zones. | [6 empty] | 1 | Nos | 218120 | 35000
4 | Supply, Installation, Testing & Commssioning of DVD Music Player with necessary accessories. | [6 empty] | 1 | Nos | 16450 | 1000
| Digital Amplifiers | [6 empty] | 0 | Heading | 0 | 0
7 | Supply, Installation, Testing & Commssioning of 1X500W Class-D Amplifier, which can provide automatic re-settable overcurrent, overload, overheating, overvoltage, under-voltage and DC protection and High Efficiency Class D Power Amplifier, 500W, 100V/70 Output, with 100 - 240 VAC input. Complaint to IEC/EN 60065:2001 (7th E) + A1:2005 = A2:2010, IEC/EN/UL 62368-1: 2014 (2nd E), EN 60065.2002 + A12006 + A11: 2008 + A2:2010 + A12:2011, EN 62368:2014, CSA C22.2 NO.62368-1-14:2014, UL 62368:2014, EN 55032:2012 with EN 55032:2012 AC 2013, EN 61000-3-2:2014, EN 61000-3-3:2013, EN 55103-2:2009, FCC part 15 subpart B | [6 empty] | 2 | Nos | 51040 | 10000
| CCTV | [6 empty] | 0 | Heading | 0 | 0
1 | Additional pricing fto change 55inch dispaly to 65inch Display | [6 empty] | 1 | Nos | 34066.6667 | 1250
2 | Supply, installation, testing and commissioning of 32Chs NVR 4K (8 MP) Support, H.265/H.264, Stream Encryption, 8 SATA, 0 TB, NON POE, RAID | [6 empty] | 1 | Nos | 361000 | 12000
3 | Additional hard disk for increasing the storage by 30 days | [6 empty] | 1 | lot | 120590 | 1250
| Door interlocking system with ACS for shower and change room | [7 empty] | Heading
1 | 4 Door interlock controller | [6 empty] | 2 | Nos. | 17640 | 3000
2 | 11 Door interlock controller | [6 empty] | 1 | Nos. | 124680 | 12000
3 | Supply, Installation, Testing and Commssioining Electromagnetic lock Single Door Leaf - 600lbs | [6 empty] | 14 | Nos. | 3850 | 1250
4 | Door Contact Sensor | [6 empty] | 14 | Nos. | 180 | 100
5 | Supply, Installation, Testing and Commssioining Emergency door release switch | [6 empty] | 17 | Nos. | 670 | 250
6 | Supply, Installation, Testing and Commssioining no touch exit switch | [6 empty] | 33 | Nos. | 1150 | 500
7 | Supply, Installation, testing and commsissioning of Server for the above ACS software | [6 empty] | 1 | Nos. | 454545.4545 | 25000
1 | Supply, Installation, testing and commsissioning of inetgration of FAS &PAS | [6 empty] | 1 | Nos. | 320000 | 60000